## SD Comments
Reviewer's Name: | Comm. No. | Drawing/ Specification Reference Number | Room/ Detail Number | Reviewer’s Comments | Architect’s/ Engineer’s Response | Status Open/Closed

## Example of Use
Reviewer's Name: | Comm. No. | Drawing/ Specification Reference Number | Room/ Detail Number | Reviewer’s Comments | Architect’s/ Engineer’s Response | Status Open/Closed
Miles Edson | 1 | A100 | Glenn Data 196 SF | This existing Glenn MDF should expanded into the 84 SQ FT space above. A portion of the wall separating would be retained as it holds the existing fiber terminations.
Miles Edson | 2 | A100 | Connector | Will the low voltage cabling for the connector go to the DATA 230SF room in north end of Glenn or into the IT 66SF room in the connector.
Miles Edson | 3 | A100 | Data Risers South Glenn | Data risers do not go all the way to attic on the south end of building.
Miles Edson | 4 | A100 | North Data Room Glenn | I don't see any risers going with the north data room. Need risers all the way to attic.
Miles Edson | 5 | A100 | Attic Glenn/Towers | Confirm data closets on basement level will be able to serve attic level without going over distance limits. 90 meters.
Miles Edson | 6 | A100 | Towers Elec 196 SF | Room label Elec 196 SF should be the main data closet for the building, not electrical.
Miles Edson | 7 | A100 | Towers Elec 196 SF | Data risers do not go all the way to attic on the south end of building.
Miles Edson | 8 | A100 | Towers | No data closet and associated risers for the north end of Towers.
Greg Spiro | 9 | Civil narrative | Site Utilities | Do not use PVC for underground domestic water & fire. Spec Ductile Iron for underground domestic water pipe 4" and up. Copper K for smaller.
Greg Spiro | 10 | Civil narrative | Site Utilities | Do not use PVC for underground sewer. Spec ductile iron.
Greg Spiro | 11 | Mechanical narrative | Mechanical | provide isolation valves and drain capabilities for chw & hw risers
Greg Spiro | 12 | Mechanical narrative | Mechanical | Provide metering and data logger for chw, steam condensate power, gas and domestic water to interface with Ion database
Greg Spiro | 13 | Mechanical narrative | Mechanical | Kitchen hoods will require fire supression system
Greg Spiro | 14 | Mechanical narrative | Mechanical | Electrical rooms to be ventilated or on base building systems. DX equipment should not be required. OA in unoccupied spaces is not required.
Greg Spiro | 15 | Mechanical & Plumbing narrative | Mechanical | All motors over 1hp to be premium efficiency
Greg Spiro | 16 | Mechanical narrative | Mechanical | chw pipe insulation to be closed cell materials.
Greg Spiro | 17 | Plumbing narrative | Plumbing | Submit boiler cut sheets to David Marder for low Nox compliance and gas consumption
Greg Spiro | 18 | Plumbing narrative | Plumbing | Flush mount WC auto sensors
Greg Spiro | 19 | Mechanical narrative | Plumbing | Controls are not specified
Greg Spiro | 20 | General | Plumbing | Will M&V credit be sought. If so an M&V plan needs to be written. Possibly by the CxA.
Jerry Young | 21 | L1.01 | Landscaping | There are several trees within the contract limits scheuled to be saved with new construction impeding root zones. There needs to be a comprhensive plan with help from certified arborist indicating specific construction process and how work will be performed. As design progresses the electrical, irrigation, civil engineers must be cognicant of these trees. All utilities should be diverted around drip line.
Jerry Young | 22 | L1.01 | Site | Electrical equipment- verify required clearance and access
Jerry Young | 23 | L1.03 | Site | Remove Catalpa Tree RA Courtyard
Jerry Young | 24 | L1.01 | Site | Please provide grading plan with contors for next submittlal.
David Chandler | 25 | L1.01/42 | Electrical | The switch (keynote 42) is no longer planned at this location. It will be located outside of the project boundary.
David Chandler | 26 | L1.02 | Landscaping / Electrical | Trees in the curb bumpout on 3rd are along the planned new ductbank route and in the immediate vicinity of a new manhole. What is the minimum cover required over ductbanks and manholes in order to accommodate the trees?
David Chandler | 27 | A100, A110 | Electrical | A100 shows a small room in Towers basement labeled "GENERATOR" plus another room labeled "EM ELEC". A110 shows a room (with no door) labeled "EMERGENCY ELECTRICAL". What is the purpose of each of these spaces? Is the sum of these spaces appropriate for the need (seems excessive)?
David Chandler | 28 | A100, A110 | Electrical | There's a large electrical room shown on the basement and the first floor of Towers. Are both really needed?
David Chandler | 29 | A110 - A140 | Electrical | What are the intended locations of branch circuit panelboards, and other items such as fire alarm NAC extenders? There do not appear to be any closets for these items.
David Chandler | 30 | Mech Narrative / 1.10 | Mechanical | Electrical rooms containing only panelboards or switchboards might not need dedicated cooling. Need to evaluate each room.
David Chandler | 31 | Plumb. Narrative / 1.2,E | Plumbing | Meter data goes to the campus metering system.
David Chandler | 32 | Elec. Narrative, 1.4, C | Electrical | The new loop switch will be located outside of the project boundary.
David Chandler | 33 | Elec. Narrative, 1.4, E | Electrical | ION 7550 is appropriate for the main, but other less expensive ION types (7350 and 6200) should be considered for submeter applications.
David Chandler | 34 | Elec. Narrative, 1.11, A | Electrical | Voice, data and CATV infrastructure is part of the project, not 'by the Owner'.
Jay Jenkins | 35 | L1.01 | Landscape / Hardscape | Remove stair from Techwood sidewalk to Glenn Courtyard
Jay Jenkins | 36 | L1.01, Typ. | Landscape / Hardscape | Avoid square sidewalk transitions (pedestrians will cut the corner)
Jay Jenkins | 37 | L1.01 | Landscape / Hardscape | Consider concrete with brick banding for serice drive / pedestrian path between Glenn and Cloudman
Jay Jenkins | 38 | L1.01 | Landscape / Hardscape | One section of bike racks is in the back up path of the garbage / recycling truck - protect or relocate
Jay Jenkins | 39 | L1.02 | Landscape / Hardscape | Lawn at Glenn courtyard facing Techwood likely not the right solution given the lack of sunlight
Jay Jenkins | 40 | L2.01, 05/08 | Landscape / Hardscape | Stormwater management system shown adjacent to building structure - adjust detail to provide buffer or relocate
Jay Jenkins | 41 | D100, 02 4199A 06 | Demo Notes | Confirm Housing to remove all equisting equipment (kitchen, etc)
Jay Jenkins | 42 | A100 | General | Basement Laundry not labeled
Jay Jenkins | 43 | A100 | General | Detail for floor drains and slope to drain for laundry rooms (all locations)
Jay Jenkins | 44 | A140 | General | Consider extending Solartubes the entire length of the corridor and add to public spaces as available - coordinate with daylighting system to dim / turn off lights
Jay Jenkins | 45 | A150 | General | Consider adding roof safety devices / tie offs for use during construction as well as after completion (none currently exist)
Jay Jenkins | 46 | Civil Narrative, 2.6 | Civil | Site construction will meet campus standard concrete with brick banding in certain areas (sidewalks along Techwood, etc)
Jay Jenkins | 47 | Mech Narrative, 1.7E | Mechanical | Explore vertical dryer exhaust vs. horizontal to eliminate multiple exterior exhaust penetrations
Jay Jenkins | 48 | Mech Narrative, 1.8E | Mechanical | Explore vertical hood exhaust vs. horizontal to eliminate multiple exterior exhaust penetrations
Jay Jenkins | 49 | Mech Narrative, 1.10A | Mechanical | Consider cooling with chilled water to eliminate exterior ground level condensing units
Jay Jenkins | 50 | Mech Narrative | 1.11.A | Consider cooling with chilled water to eliminate exterior ground level condensing units
Jay Jenkins | 51 | Mech Narrative | TYP | All outside air to be treated with preheat / reheat to remove humidity
Jay Jenkins | 52 | Mech Narrative |  | Project will be phased with Phase I (Towers) to be complete and independantly operating while Phase II (Glenn) is under construction. All mech systems necessary to operate Phase I shall be complete and operate independently at the conclusion of Phase I.
Jay Jenkins | 53 | Plumbing Narrative | 1.5.C. | Laundry Rooms should also include floor drains.
Jay Jenkins | 54 | Electrical Narrative | 1.11.A. | Contractor will be responsible for low voltage infrastructure installation, not owner.
Glen Hickman | 55 |  | Telecom Rooms | Please note the new rooms in the attic. I'm not sure if the cabling to these spaces will be over spec? Might need a Telecom Room is attic? Also, the drawings indicate the 2nd Glenn Telecom Closet is going to be demo'ed for the elevator. They new plan do show a new Telecom Room closet to that space.
Glen Hickman | 56 |  | Wireless Network | Network equipment and wireless APs will be reused. We might need a few more APs for the attic space.
Glen Hickman | 57 | D100 |  | An existing telecom room is shown being demo'ed. Need to note the removal of the existing CATV cable, since that could affect the existing system that feed other Area 1 and Area 2 Residence Halls.
Glen Hickman | 58 | A140 |  | Verify telecom cable lengths to telecom rooms in basement for new rooms in attics. May have to have telecom room in attic due to cable lengths?
Housing Page Turning | 59 |  | Accoustical Panels | Accoustical panels in stairs. Housing has a standard... we will get this information to you.
Housing Page Turning | 60 |  | Bathroom | Bathroom design needs to be addressed. Two urinals to be added. Unisex / ADA bathroom on each floor. Possible compression of vestibule. Leave space for shelving for student costmetic baskets.
Housing Page Turning | 61 |  | Bathroom | All sinks must have stoppers.
Housing Page Turning | 62 |  | Bathroom | Basis of design for toilets to be Toto.
Housing Page Turning | 63 |  | Bathroom | Showers are to be solid surface surround and pan. Transolid is a preferred vendor.
Housing Page Turning | 64 |  | Bathroom | Bathroom sinks and counters are to be solid surface.
Housing Page Turning | 65 |  | Bicycle Storage | No interest in sacrificing a room for bicycle storage at the interior.
Housing Page Turning | 66 |  | Controls | Housing prefers that controls be competatively bid (ie not necessarily JCI).
Housing Page Turning | 67 |  | Demo Notes | Note on the drawings that wireless (WIFI)system and buzzcard system and components needs to be carefully removed and reinstalled.
Housing Page Turning | 68 |  | Dormer Design | Harris style dormer is prefered by Housing. The Harris dormers are an addition to an existing building.
Housing Page Turning | 69 |  | Electrical | Emergency power should cover lights, elevators and TVs! No battery packs.
Housing Page Turning | 70 |  | Electrical | BAS infrastructure should be in place for energy monitoring that can be communicated to the students.
Housing Page Turning | 71 |  | Electrical | Metering information is in the GT yellowbook.
Housing Page Turning | 72 |  | Fitness Room | Provide final space dimensions for fitness room and GT can provide an equipment layout from Campus Recreation.
Housing Page Turning | 73 |  | Furniture Budget | Bob Canada to provide Kim with updated furniture budget. Fitness equipment should be carried in this budget.
Housing Page Turning | 74 |  | Furniture for Common Areas | North Avenue furniture is standard for common areas. Housing to provide information on this.
Housing Page Turning | 75 |  | Kitchen | Break room to be enclosed with glass. Open scheme to hallway is not approved.
Housing Page Turning | 76 |  | Kitchen | Kitchen sinks are to be undermount.
Housing Page Turning | 77 |  | Kitchen | Confirmed full kitchen stove requirement but the option for counter top cooktop unit and under counter oven open for consideration (cleaner ADA accessibility) in lieu of full size range.
Housing Page Turning | 78 |  | Kitchen | The range should be at counter height - which requires a drop in range - its Not a separate cooktop and oven.
Housing Page Turning | 79 |  | Kitchen | Approved to leave wall between break room and kitchen open.
Housing Page Turning | 80 |  | Kitchens | Full stove with oven is intent for kitchens on each floor. Confirmed.
Housing Page Turning | 81 |  | Kitchens | Ice machine to not be the scoop type. Needs to be full size with dispenser. Housing has a standard... we will get this to you.
Housing Page Turning | 82 |  | Landscaping | Housing has requested irrigation at landscaping. Full irrigation at grass, drip or bubblers at other areas.
Housing Page Turning | 83 |  | Landscaping | Courtyard grass lawn extent of full irrigation, remaining landscape areas to be drip or bubblers at least through plant establishment. Long term these areas should not require/be irrigated.
Housing Page Turning | 84 |  | Laundry | There should not be a door between the laundry room and the adjacent study room.
Housing Page Turning | 85 |  | Laundry | Folding area at laundry should be fixed similar to what was done at FFM. Fixed over washers.
Housing Page Turning | 86 |  | Lighting | Motion sensors at all common area and corridor lights (Verve system). Housing had problems with bathrooms and frequency of use. (Jay, please elaborate?)
Housing Page Turning | 87 |  | Multi Purpose Room | Sliding door example for multi-purpose room is at Center Street. Kim to take a photo.
Housing Page Turning | 88 |  | Staff Offices | Office locations: One each in Glenn and Towers. Sacrifice a room for this in Glenn. Large work room in Towers.
Housing Page Turning | 89 |  | Study Areas | MEP space should not take away from study area. Study area should be rectangular, not square. Take up seating area as needed to reconfigure.
Housing Page Turning | 90 |  | Study Room | There should be a white board in each study room.
Housing Page Turning | 91 |  | Vending Area | Kim Wilson to get vending information from Rich Steele. Vending will likely be centrally located in the connector. Typically it is not located above the first floor of Housing buildings, but could be located in laundry rooms.
Housing Page Turning | 92 |  | Water Filling Station | Housing has a standard water bottle filling station.... we will get this information to you.
Housing Page Turning | 93 |  | Stairs | Add accoustical panels in stairs.
Housing Page Turning | 94 |  | Classrooms | Rename classroom to 'learning center'
Housing Page Turning | 95 |  | Landscaping | Show locations of grills on site.
Gary Jelin | 96 | Specs |  | Include preliminary LEED Checklist.
Gary Jelin | 97 | T001 |  | Add project team members under "Project Team" heading.
Gary Jelin | 98 | A001 |  | Under "Building Program" list complete residence hall program and include list of total sleeping rooms
Gary Jelin | 99 | A002 |  | Provide key plan with views noted.
Gary Jelin | 100 | A100 |  | Label all rooms. Indicate door openings in elevator. Indicate travel direction on stairs.
Gary Jelin | 101 | A110 |  | Enclose Lounge with walls. Indicate travel directions on stairs. Confirm door locations in all rooms where doors are not shown. Delete door between Study and Laundry. Add urinals in bathrooms.
Gary Jelin | 102 | A120 |  | See comments on A110.
Gary Jelin | 103 | A201 |  | Indicate floor level reference elevations. Add material notes to connector building on Elevation no. 2.
Gary Jelin | 104 | A202 |  | Indicate floor reference elevations. Note existing materials.
Gary Jelin | 105 | A211 |  | Delete shadows from building sections.Indicate floor level reference elevations. Preliminary wall sections at connector?
Gary Jelin | 106 | A411 |  | Confirm final location for fan coil units. Does proposed elevator require a machine room?
Gary Jelin | 107 | A413 |  | At First Floor Plan use sliding glass doors at Multi-Purpose Room in lieu of folding glass wall.
Gary Jelin | 108 | A601 |  | Confirm if there is a corridor door at the Bath vestibule. Floor Plan graphics are not consistent.